## Single Unit Sample Sheet
TOSHIBA AIR CONDITIONING
Digital Inverter / Super Digital Inverter - ver c1.4
(Single Split System)
Site/Store Name | 1 High Street, Warblington on Sea, Sussexshire AB12 3DE- store N° 9999
Site Address
Commissioning Date | 29th Feb 1940
Installation company | Jones Refrigeration
Address | 42 Main Road, Cheam, London, FG45 6HJ
Telephone | 01234 567890
e-mail | jones @ jonesref . Co . uk
Commissioning Engineer | Arthur Hightess
Training Certificate Number | T120R
Please forward to:
commissioning.uk@toshiba-ac.com
Local Controller Model | RBC-AMT32E
Local Controller location | Managers office
Sub controller model and location | N/A
Central Controller Model | TCB-SC642TLE2
Weekly Timer model | TCB-EXS21TLE
Time switch settings | 07.30 - 18.00 Mon to Sat (closed Sunday)
Network cable | 1.5mm² 2-core screened cable
Room sensor used? Location? | Standard return air
Configured for auto restart? | No
Configured for controller temp. sensor? | No
Indoor model RAV-SM****T*-E | SM1104U
Indoor serial number | 91234567
Indoor location or reference | Sales Area
Outdoor model RAV-SM/SP****AT-E | SP1104
Outdoor serial number | 90123456
Outdoor location or reference | Rear of shop
Distribution board reference | BD123
Fuse size and type | 16A type C
Network address set from….. | Protocol PCB
Support and insulation effective | Yes
Condensate removal ok | Yes
External pump fitted | No
Protocol converter fitted | Yes
Outdoor unit energised for 12 hours | Yes
Refrigeration circuit
Strength tested to F-Gas regulation | Yes
Leak tested to F-Gas regulation | Yes
Vacuum achieved | 20 Torr
Maintained for 30 minutes | Yes
Refrigerant
Refrigerant type | R410a
Suction pipe size | 5/8
Liquid pipe size | 3/8
Refrigerant circuit length | 48m
Additional refrigerant added (kg) | 0.72
Factory refrigerant charge (kg) | 3.1
Total system refrigerant charge (kg) | 3.82
Running tests (C/H) @ test condition | Cooling Mode | Heating Mode
02 return air temperature | 25 | 20
03 indoor coil - liquid temperature | -20 | 64
04 indoor coil - vapour temperature | -15 | 74
60 outdoor coil - liquid temperature | 25 | -5
61 ambient temperature | 28 | 28
62 compressor discharge temperature | 120 | 119
63 compressor suction temperature | 28 | 29
Supply air temperature | 8 | 41
Voltage across terminals L-N | 230 | 230
Running current | 1.2 | 3.1
Configurable items
03 network address | 0002
12 outdoor number | 0001
13 indoor unit number | 0001
14 indoor unit role | 0000
19 louver functions | 0004
5d air flow correction | 0000
Comments | The above figures in Run Test and Config Item are not representative - do not copy them
Toshiba Air Conditioning, UTC House, Guildford Road, Leatherhead KT22 9UT Tel: 0870 8430333

## Single Unit
TOSHIBA AIR CONDITIONING
Digital Inverter / Super Digital Inverter - ver c1.4
(Single Split System)
Site/Store Name | TBC
Site Address | TBC
Commissioning Date | TBC
Installation company | TBC
Address | TBC
Telephone | TBC
e-mail | TBC
Commissioning Engineer | TBC
Training Certificate Number | TBC
Please forward to:
commissioning.uk@toshiba-ac.com
Local Controller Model | TBC
Local Controller location | TBC
Sub controller model and location | TBC
Central Controller Model | TBC
Weekly Timer model | TBC
Time switch settings | TBC
Network cable (used with Central Controller) | TBC
Room sensor used? Location? | Yes / No
Configured for auto restart? | Yes / No
Configured for controller temp. sensor? | Yes / No
Indoor model RAV-SM****T*-E | TBC
Indoor serial number | TBC
Indoor location or reference | TBC
Outdoor model RAV-SM/SP****AT-E | TBC
Outdoor serial number | TBC
Outdoor location or reference | TBC
Distribution board reference | TBC
Fuse size and type | TBC
Network address set from….. | TBC
Support and insulation effective | Yes / No
Condensate removal ok | Yes / No
External pump fitted | Yes / No
Protocol converter fitted | Yes / No
Outdoor unit energised for 12 hours | Yes / No
Refrigeration circuit
Strength tested under F-gas legislation | Yes / No
Leak tested under F-gas legislation | Yes / No
Vacuum achieved | TBC
Maintained for 30 minutes | Yes / No
Refrigerant
Refrigerant type | TBC
Suction pipe size | TBC
Liquid pipe size | TBC
Refrigerant circuit length | TBC
Additional refrigerant added (kg) | 0
Factory refrigerant charge (kg) | 0
Total system refrigerant charge (kg) | 0
Running tests (C/H) @ test condition | Cooling Mode | Heating Mode
02 return air temperature | Required | Required
03 indoor coil - liquid temperature | Required | Required
04 indoor coil - vapour temperature | Required | Required
60 outdoor coil - liquid temperature | Required | Required
61 ambient temperature | Required | Required
62 compressor discharge temperature | Required | Required
63 compressor suction temperature | Required | Required
supply air temperature (HEAT & COOL) | Required | Required
Voltage across terminals L-N | Required | Required
Running current | Required | Required
Configurable items
03 network address | Required
12 outdoor number | Required
13 indoor unit number | Required
14 indoor unit role | Required
19 louver functions | Required
5d air flow correction | Required
Comments
Toshiba Air Conditioning, UTC House, Guildford Road, Leatherhead KT22 9UT Tel: 0870 8430333
Note on B4: Enter full site/store name
Note on B5: Enter full site address
Note on B21: Each day may be programmed separately, with up to 3 operating periods per day - if using scheduled timer
Note on B22: The network cable should be terminated in the indoor unit with Protocol Converter fitted. The screen shall be continuous and earthed at a single point. Minimum 1.5mm² up to 500m, 2.0mm² over 500m If a Protocol Converter has not been fitted, the cable should be left with enough slack for future use.
Note on B23: A single room sensor can be added to the group wiring and will provide the temperature value for the entire group. Configuration item 32 must remain at 0000
Note on B24: To enable group auto-restart, configuration item 28 to 0001.
Note on B25: Provides operating temperature value for the entire group. Configuration item 32 must be set to 0001. If the temperature sensor is enabled, the controller must be located in a representative position.
Note on B27: The style letter in the model number must be included i.e. 1104U = cassette, 1406B = ducted, 866K = hi-wall, 1107C = under-ceiling.
Note on B30: Identify Type of Outdoor Unit SM=Standard Digital Inverter SP=Super Digital Inverter
Note on B34: Suggested breaker sizes: SM56* - 16A SM80* - 16A SM110* - 20A SM140* - 25A SM160* - 32A SM2244 - 16A SM2804 - 20A SP40* - 10A SP56* - 16A SP80* - 16A SP110* - 16A SP140* - 25A SP110*AT8 - 10A SP140*AT8 - 16A SP160*AT8 - 16A
Note on B35: if applicable
Note on B36: Both liquid and vapour lines require full insulation (0 or 1 class).
Note on B37: Check that condensate is drained effectively. Circle PUMP if an external lift pump is used.
Note on B39: Only necessary for network control. A group will only have only one protocol converter fitted within the HEADER indoor unit.
Note on B40: Mains voltage should be supplied to the outdoor unit as soon as practical to warm the compressor.
Note on B42: Pressure should be increased in 3 stages - to ensure that the leak test may be conducted safely. Strength tested to not less than 1.3 x M.W.P
Note on B43: No maximum time for the leak test but there will be no drop in pressure during a successful test. Leak tested to 1.0 - 1.1 x M.W.P
Note on B44: The vacuum required will be dependant on the average temperature of the system (halfway between indoor and outdoor temperatures) A minimum of 4 Torr (530 Pa) should be achieved in all cases however, If the average temperature is below 10ºC a vacuum of 2 Torr (400 Pa) must be achieved. 5ºC requires a vacuum of a least 3 Torr (260 Pa) When below freezing point, the system cannot be reliably dehydrated
Note on B48: When systems are installed on 'existing' R22/R407c pipe work and the suction pipe is one step larger than standard, follow the 'Existing Pipe' instructions found within installation manual.
Note on B50: The linear (actual) length of the refrigeration circuit. SM563/SM803 maximum is 30m SM1103/SM1403/SM1603 maximum 50m SP564 & SP804 maximum is 50m SP1104 & SP1404 maximum is 75m SM2244 & SM2804 maximum 70m Note: there is a minimum length of 5m for all models above. SM2244 & 2804 have minimum separation of 7.5m
Note on B51: Only required when the circuit length exceeds the precharged pipe length. SM563/SP564 & SM803 are precharged to 20m. SM1103/SM1403/SM1603/SP804/SP1104 & SP1404 are precharged to 30m. SM2204/2804 are precharged to 30m Additional amounts; All 56* models use 20g/m All 80*/110*/140* & 160* models use 40g/m All 2244/2804 models 80g/m Always refer to installation manual
Note on B52: Factory refrigerant charge can be found on the name plate of the outdoor unit.
Note on B53: Total system charge is the additional charge plus the factory charge.
Note on B54: To initiate Press CHECK(Test) for 4 seconds. When the controller displays TEST, use mode to select heat or cool and use UNIT to choose the system to be tested. Note - systems MUST be tested individually. Values for both heating and cooling operations should be shown. This does not provide a 100% demand. To check values during test, (after compressor operation has started), press CHECK(Test)+CLEAR(CL). Press CHECK(Test) to terminate the test.
Note on B62: The temperature (DB) of the air supplied during the cooling and heating processes. Also known as air outlet temperature.
Note on B63: This measurement should be taken while the compressor is running.
Note on B64: Input current is limited by the inverter.
Note on B65: To access: Press CHECK(Test) & SET & CL buttons for 4 seconds
Note on B66: Only necessary when network control is used. Factory default 0099 May be set from the remote controller, through configuration item 03.
Note on B67: Automatically addressed though may be changed to reflect site reference.
Note on B68: Automatic addressing - generally 0001 unless twinned indoor units are used.
Note on B69: Individual system = 0000 Control group Header = 0001 (only 1 lead unit within a group) Follower = 0002 (up to a maximum of 7 followers)

## 8 Units
TOSHIBA AIR CONDITIONING
Digital Inverter / Super Digital Inverter - ver c1.4
(Multiples of standard split systems)
Site/Store Name | TBC
Site Address | TBC
Commissioning Date | TBC
Installation company | TBC
Address | TBC
Telephone | TBC
e-mail | TBC
Commissioning Engineer | TBC
Training Certificate Number | TBC
Please forward to:
commissioning.uk@toshiba-ac.com
Local Controller Model | TBC
Local Controller location | TBC
Sub controller model and location | TBC
Central Controller Model | TBC
Weekly Timer model | TBC
Time switch settings | TBC
Network cable (used with Central Controller) | TBC
Room sensor used? Location? | Yes / No
Configured for auto restart? | Yes / No
Configured for controller temp. sensor? | Yes / No
System number | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Indoor model RAV-SM****T*-E | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
Indoor serial number | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
Indoor location or reference | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
Outdoor model RAV-SM/SP***AT-E | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
Outdoor serial number | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
Outdoor location or reference | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
Distribution board reference | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
Fuse size and type | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
Network address set from….. | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
Support and insulation effective | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No
Condensate removal ok | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No
External pump fitted | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No
Protocol converter fitted | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No
Outdoor unit energised for 12 hours | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No
Refrigeration circuit
Strength tested under F-gas legislation | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No
Leak tested under F-gas legislation | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No
Vacuum achieved | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
Maintained for 30 minutes | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No
Refrigerant
Refrigerant type | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
Suction pipe size | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
Liquid pipe size | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
Refrigerant circuit length | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
Additional refrigerant added (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Factory refrigerant charge (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total system refrigerant charge (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Running tests (C/H) @ test condition | Cool / Heat | Cool / Heat | Cool / Heat | Cool / Heat | Cool / Heat | Cool / Heat | Cool / Heat | Cool / Heat
02 return air temperature | Required | Required | Required | Required | Required | Required | Required | Required
03 indoor coil - liquid temperature | Required | Required | Required | Required | Required | Required | Required | Required
04 indoor coil - vapour temperature | Required | Required | Required | Required | Required | Required | Required | Required
60 outdoor coil - liquid temperature | Required | Required | Required | Required | Required | Required | Required | Required
61 ambient temperature | Required | Required | Required | Required | Required | Required | Required | Required
62 compressor discharge temperature | Required | Required | Required | Required | Required | Required | Required | Required
63 compressor suction temperature | Required | Required | Required | Required | Required | Required | Required | Required
supply air temperature (HEAT & COOL) | Required | Required | Required | Required | Required | Required | Required | Required
Voltage across terminals L-N | Required | Required | Required | Required | Required | Required | Required | Required
Running current | Required | Required | Required | Required | Required | Required | Required | Required
Configurable items
03 network address | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
12 outdoor number | Required | Required | Required | Required | Required | Required | Required | Required
13 indoor unit number | Required | Required | Required | Required | Required | Required | Required | Required
14 indoor unit role | Required | Required | Required | Required | Required | Required | Required | Required
19 louver functions | Required | Required | Required | Required | Required | Required | Required | Required
5d air flow correction | Required | Required | Required | Required | Required | Required | Required | Required
Comments
Toshiba Air Conditioning, UTC House, Guildford Road, Leatherhead KT22 9UT Tel: 0870 8430333
Note on B4: Enter full site/store name
Note on B5: Enter full site address
Note on B21: Each day may be programmed separately, with up to 3 operating periods per day - if using scheduled timer
Note on B22: The network cable should be terminated in the indoor unit with Protocol Converter fitted. The screen shall be continuous and earthed at a single point. Minimum 1.5mm² up to 500m, 2.0mm² over 500m If a Protocol Converter has not been fitted, the cable should be left with enough slack for future use.
Note on B23: A single room sensor can be added to the group wiring and will provide the temperature value for the entire group. Configuration item 32 must remain at 0000
Note on B24: To enable group auto-restart, configuration item 28 to 0001.
Note on B25: Provides operating temperature value for the entire group. Configuration item 32 must be set to 0001. If the temperature sensor is enabled, the controller must be located in a representative position.
Note on B28: The style letter in the model number must be included i.e. 1104U = cassette, 1406B = ducted, 866K = hi-wall, 1107C = under-ceiling.
Note on B31: Identify Type of Outdoor Unit SM=Standard Digital Inverter SP=Super Digital Inverter
Note on B35: Suggested breaker sizes: SM56* - 16A SM80* - 16A SM110* - 20A SM140* - 25A SM160* - 32A SM2244 - 16A SM2804 - 20A SP40* - 10A SP56* - 16A SP80* - 16A SP110* - 16A SP140* - 25A SP110*AT8 - 10A SP140*AT8 - 16A SP160*AT8 - 16A
Note on B36: if applicable
Note on B37: Both liquid and vapour lines require full insulation (0 or 1 class).
Note on B38: Check that condensate is drained effectively. Circle PUMP if an external lift pump is used.
Note on B40: Only necessary for network control. A group will only have only one protocol converter fitted within the HEADER indoor unit.
Note on B41: Mains voltage should be supplied to the outdoor unit as soon as practical to warm the compressor.
Note on B43: Pressure should be increased in 3 stages - to ensure that the leak test may be conducted safely. Strength tested to not less than 1.3 x M.W.P
Note on B44: No maximum time for the leak test but there will be no drop in pressure during a successful test. Leak tested to 1.0 - 1.1 x M.W.P
Note on B45: The vacuum required will be dependant on the average temperature of the system (halfway between indoor and outdoor temperatures) A minimum of 4 Torr (530 Pa) should be achieved in all cases however, If the average temperature is below 10ºC a vacuum of 2 Torr (400 Pa) must be achieved. 5ºC requires a vacuum of a least 3 Torr (260 Pa) When below freezing point, the system cannot be reliably dehydrated
Note on B49: When systems are installed on 'existing' R22/R407c pipe work and the suction pipe is one step larger than standard, follow the 'Existing Pipe' instructions found within installation manual.
Note on B51: The linear (actual) length of the refrigeration circuit. SM563/SM803 maximum is 30m SM1103/SM1403/SM1603 maximum 50m SP564 & SP804 maximum is 50m SP1104 & SP1404 maximum is 75m SM2244 & SM2804 maximum 70m Note: there is a minimum length of 5m for all models above. SM2244 & 2804 have minimum separation of 7.5m
Note on B52: Only required when the circuit length exceeds the precharged pipe length. SM563/SP564 & SM803 are precharged to 20m. SM1103/SM1403/SM1603/SP804/SP1104 & SP1404 are precharged to 30m. SM2204/2804 are precharged to 30m Additional amounts; All 56* models use 20g/m All 80*/110*/140* & 160* models use 40g/m All 2244/2804 models 80g/m Always refer to installation manual
Note on B53: Factory refrigerant charge can be found on the name plate of the outdoor unit.
Note on B54: Total system charge is the additional charge plus the factory charge.
Note on B55: To initiate Press CHECK(Test) for 4 seconds. When the controller displays TEST, use mode to select heat or cool and use UNIT to choose the system to be tested. Note - systems MUST be tested individually. Values for both heating and cooling operations should be shown. This does not provide a 100% demand. To check values during test, (after compressor operation has started), press CHECK(Test)+CLEAR(CL). Press CHECK(Test) to terminate the test.
Note on B63: The temperature (DB) of the air supplied during the cooling and heating processes. Also known as air outlet temperature.
Note on B64: This measurement should be taken while the compressor is running.
Note on B65: Input current is limited by the inverter.
Note on B66: To access: Press CHECK(Test) & SET & CL buttons for 4 seconds
Note on B67: Only necessary when network control is used. Factory default 0099 May be set from the remote controller, through configuration item 03.
Note on B68: Automatically addressed though may be changed to reflect site reference.
Note on B69: Automatic addressing - generally 0001 unless twinned indoor units are used.
Note on B70: Individual system = 0000 Control group Header = 0001 (only 1 lead unit within a group) Follower = 0002 (up to a maximum of 7 followers)

## Twin Splits
TOSHIBA AIR CONDITIONING
Digital Inverter / Super Digital Inverter - ver c1.4
(Up to 4 x Twin-Split split systems)
Site/Store Name | TBC
Site Address | TBC
Commissioning Date | TBC
Installation company | TBC
Address | TBC
Telephone | TBC
e-mail | TBC
Commissioning Engineer | TBC
Training Certificate Number | TBC
Please forward to:
commissioning.uk@toshiba-ac.com
Local Controller Model | TBC
Local Controller location | TBC
Sub controller model and location | TBC
Central Controller Model | TBC
Weekly Timer model | TBC
Time switch settings | TBC
Network cable (used with Central Controller) | TBC
Room sensor used? Location? | Yes / No
Configured for auto restart? | Yes / No
Configured for controller temp. sensor? | Yes / No
Indoor number | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2
Indoor model RAV-SM****T*-E | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
Indoor serial number | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
Indoor location or reference | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
Outdoor model RAV-SM/SP***AT-E | TBC |  | TBC |  | TBC |  | TBC
Outdoor serial number | TBC |  | TBC |  | TBC |  | TBC
Outdoor location or reference | TBC |  | TBC |  | TBC |  | TBC
Distribution board reference | TBC |  | TBC |  | TBC |  | TBC
Fuse size and type | TBC |  | TBC |  | TBC |  | TBC
Network address set from….. | TBC |  | TBC |  | TBC |  | TBC
Support and insulation effective | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No
Condensate removal ok | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No
External pump fitted | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No
Protocol converter fitted | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No
Outdoor unit energised for 12 hours | Yes No |  | Yes No |  | Yes No |  | Yes No
Refrigeration circuit
Strength tested under F-gas legislation | Yes No |  | Yes No |  | Yes No |  | Yes No
Leak tested under F-gas legislation | Yes No |  | Yes No |  | Yes No |  | Yes No
Vacuum achieved | TBC |  | TBC |  | TBC |  | TBC
Maintained for 30 minutes | Yes No |  | Yes No |  | Yes No |  | Yes No
Refrigerant
Refrigerant type | TBC |  | TBC |  | TBC |  | TBC
Suction pipe size | TBC |  | TBC |  | TBC |  | TBC
Pipe Sizes (Branch) | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
Refrigerant circuit length - main pipes | TBC |  | TBC |  | TBC |  | TBC
Refrigerant circuit length - branch pipes | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
Additional refrigerant added | 0 |  | 0 |  | 0 |  | 0
Factory refrigerant charge (kg) | 0 |  | 0 |  | 0 |  | 0
Total system refrigerant charge (kg) | 0 |  | 0 |  | 0 |  | 0
Running tests (C/H) @ test condition | Cool / Heat | Cool / Heat | Cool / Heat | Cool / Heat | Cool / Heat | Cool / Heat | Cool / Heat | Cool / Heat
02 return air temperature | Required | Required | Required | Required | Required | Required | Required | Required
03 indoor coil - liquid temperature | Required | Required | Required | Required | Required | Required | Required | Required
04 indoor coil - vapour temperature | Required | Required | Required | Required | Required | Required | Required | Required
60 outdoor coil - liquid temperature | Required |  | Required |  | Required |  | Required
61 ambient temperature | Required |  | Required |  | Required |  | Required
62 compressor discharge temperature | Required |  | Required |  | Required |  | Required
63 compressor suction temperature | Required |  | Required |  | Required |  | Required
supply air temperature (HEAT & COOL) | Required | Required | Required | Required | Required | Required | Required | Required
Voltage across terminals L-N | Required |  | Required |  | Required |  | Required
Running current | Required |  | Required |  | Required |  | Required
Configurable items
03 network address | TBC |  | TBC |  | TBC |  | TBC
12 outdoor number | Required |  | Required |  | Required |  | Required
13 indoor unit number | Required | Required | Required | Required | Required | Required | Required | Required
14 indoor unit role | Required | Required | Required | Required | Required | Required | Required | Required
19 louver functions | Required | Required | Required | Required | Required | Required | Required | Required
5d air flow correction | Required | Required | Required | Required | Required | Required | Required | Required
Comments | Please read comments on pipe runs and pre-charge amounts for twin splits
Toshiba Air Conditioning, UTC House, Guildford Road, Leatherhead KT22 9UT Tel: 0870 8430333
Note on B4: Enter full site/store name
Note on B5: Enter full site address
Note on B21: Each day may be programmed separately, with up to 3 operating periods per day - if using scheduled timer
Note on B22: The network cable should be terminated in the indoor unit with Protocol Converter fitted. The screen shall be continuous and earthed at a single point. Minimum 1.5mm² up to 500m, 2.0mm² over 500m If a Protocol Converter has not been fitted, the cable should be left with enough slack for future use.
Note on B23: A single room sensor can be added to the group wiring and will provide the temperature value for the entire group. Configuration item 32 must remain at 0000
Note on B24: To enable group auto-restart, configuration item 28 to 0001.
Note on B25: Provides operating temperature value for the entire group. Configuration item 32 must be set to 0001. If the temperature sensor is enabled, the controller must be located in a representative position.
Note on B28: The style letter in the model number must be included i.e. 1104U = cassette, 1406B = ducted, 866K = hi-wall, 1107C = under-ceiling.
Note on B31: Identify Type of Outdoor Unit SM=Standard Digital Inverter SP=Super Digital Inverter
Note on B35: Suggested breaker sizes: SM110* - 20A SM140* - 25A SM160* - 32A SM2244 - 16A SM2804 - 20A SP110* - 16A SP140* - 25A SP110*AT8 - 10A SP140*AT8 - 16A SP160*AT8 - 16A
Note on B36: if applicable
Note on B37: Both liquid and vapour lines require full insulation (0 or 1 class).
Note on B38: Check that condensate is drained effectively. Circle PUMP if an external lift pump is used.
Note on B40: Only necessary for network control. A group will only have only one protocol converter fitted within the HEADER indoor unit.
Note on B41: Mains voltage should be supplied to the outdoor unit as soon as practical to warm the compressor.
Note on B43: Pressure should be increased in 3 stages - to ensure that the leak test may be conducted safely. Strength tested to not less than 1.3 x M.W.P
Note on B44: No maximum time for the leak test but there will be no drop in pressure during a successful test. Leak tested to 1.0 - 1.1 x M.W.P
Note on B45: The vacuum required will be dependant on the average temperature of the system (halfway between indoor and outdoor temperatures) A minimum of 4 Torr (530 Pa) should be achieved in all cases however, If the average temperature is below 10ºC a vacuum of 2 Torr (400 Pa) must be achieved. 5ºC requires a vacuum of a least 3 Torr (260 Pa) When below freezing point, the system cannot be reliably dehydrated
Note on B49: When systems are installed on 'existing' R22/R407c pipe work and the suction pipe is one step larger than standard, follow the 'Existing Pipe' instructions found within installation manual.
Note on B51: The linear (actual) length of the refrigeration pipe work between the outdoor unit and the 'T' piece Note RAV-SM/SP110*-140*-1603AT-E Max total pipe run is 50m (main + longest branch) irrespective of outdoor unit model Max length of a single branch must not exceed 15m, subtractive difference between branch lengths must not exceed 10m. RAV-SM2244-2804AT-E Max total pipe run is 70m (main + longest branch) irrespective of outdoor unit model Max length of a single branch must not exceed 20m, subtractive difference between branch lengths must not exceed 10m.
Note on B52: The total linear (actual) length of the refrigeration circuit - from 'T' to each indoor unit. Note RAV-SM/SP110*-140*-1603AT-E Max total pipe run is 50m (main + longest branch) irrespective of outdoor unit model Max length of a single branch must not exceed 15m, subtractive difference between branch lengths must not exceed 10m. RAV-SM2244-2804AT-E Max total pipe run is 70m (main + longest branch) irrespective of outdoor unit model Max length of a single branch must not exceed 20m, subtractive difference between branch lengths must not exceed 10m.
Note on B53: Only required when the circuit length exceeds the 22 or 32 metre precharged amount. Calculation is DI/SDI For 110*AT outdoor units with 2 x 56* indoors (L1) Main Pipe minus 18m x 0.04kg/m = + (L2) Branch 1 minus 2m x 0.02kg/m = + (L3) Branch 2 minus 2m x 0.02kg/m = + Additional charge =________ kg For 140*AT & for 1603AToutdoor units with 2 x 80* indoors (L1) Main Pipe minus 18m x 0.04kg/m = + (140* sized CDU) or (L1) Main Pipe minus 28m x 0.04kg/m = + (160* sized CDU) (L2) Branch 1 minus 2m x 0.04kg/m = + (L3) Branch 2 minus 2m x 0.04kg/m = + Additional charge =________ kg DI Big For 2244-2804AT outdoor units with 2 x 110*-140* indoors (L1) Main Pipe minus 28m x 0.08kg/m = + (L2) Branch 1 minus 2m x 0.04kg/m = + (L3) Branch 2 minus 2m x 0.04kg/m = + Additional charge =________ kg Note DI/SDI range Min pipe run is 5m total Max run is 50m total irrespective of outdoor unit (L1 + L2 or L1 + L3) DI Big Range Min pipe run 7.5m total Max run is 70m total (L1 + L2 or L1 + L3) Always refer to the 'twin-kit' or installation manual
Note on B54: Factory refrigerant charge can be found on the name plate of the outdoor unit.
Note on B55: Total system charge is the additional charge plus the factory charge.
Note on B56: To initiate Press CHECK(Test) for 4 seconds. When the controller displays TEST, use mode to select heat or cool and use UNIT to choose the system to be tested. Note - systems MUST be tested individually. Values for both heating and cooling operations should be shown. This does not provide a 100% demand. To check values during test, (after compressor operation has started), press CHECK(Test)+CLEAR(CL). Press CHECK(Test) to terminate the test.
Note on B64: The temperature (DB) of the air supplied during the cooling and heating processes. Also known as air outlet temperature.
Note on B65: This measurement should be taken while the compressor is running.
Note on B66: Input current is limited by the inverter.
Note on B67: To access: Press CHECK(Test) & SET & CL buttons for 4 seconds
Note on B68: Only necessary when network control is used. Factory default 0099 May be set from the remote controller, through configuration item 03.
Note on B69: Automatically addressed though may be changed to reflect site reference.
Note on B70: Automatic addressing - generally 0001 unless twinned indoor units are used.
Note on B71: Individual system = 0000 Control group Header = 0001 (only 1 lead unit within a group) Follower = 0002 (up to a maximum of 7 followers)
Note on C51: L1- From condenser to T piece
Note on C52: L2 - From T piece to indoor
Note on D52: L3 - From T piece to indoor
Note on E51: L1- From condenser to T piece
Note on E52: L2 - From T piece to indoor
Note on F52: L3 - From T piece to indoor
Note on G51: L1- From condenser to T piece
Note on G52: L2 - From T piece to indoor
Note on H52: L3 - From T piece to indoor
Note on I51: L1- From condenser to T piece
Note on I52: L2 - From T piece to indoor
Note on J52: L3 - From T piece to indoor

## Triple Splits
TOSHIBA AIR CONDITIONING
Digital Inverter / Super Digital Inverter - ver c1.4
(Up to 2 x Triple-Split split systems)
Site/Store Name | TBC
Site Address | TBC
Commissioning Date | TBC
Installation company | TBC
Address | TBC
Telephone | TBC
e-mail | TBC
Commissioning Engineer | TBC
Training Certificate Number | TBC
Please forward to:
commissioning.uk@toshiba-ac.com
Local Controller Model | TBC
Local Controller Location | TBC
Sub controller model and location | TBC
Central Controller Model | TBC
Weekly Timer model | TBC
Time switch settings | TBC
Network cable (used with Central Controller) | TBC
Room sensor used? Location? | Yes / No
Configured for auto restart? | TBC
Configured for controller temp. sensor? | TBC
Indoor number | 1 | 2 | 3 | 1 | 2 | 3
Indoor model RAV-SM/SP****T-E | TBC | TBC | TBC | TBC | TBC | TBC
Indoor serial number | TBC | TBC | TBC | TBC | TBC | TBC
Indoor location or reference | TBC | TBC | TBC | TBC | TBC | TBC
Outdoor model RAV-SM/SP***AT-E | TBC |  |  | TBC
Outdoor serial number | TBC |  |  | TBC
Outdoor location or reference | TBC |  |  | TBC
Distribution board reference | TBC |  |  | TBC
Fuse size and type | TBC |  |  | TBC
Network address set from….. | TBC |  |  | TBC
Support and insulation effective | Yes No |  |  | Yes No
Condensate removal ok | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No
External pump fitted | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No
Protocol converter fitted | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No
Outdoor unit energised for 12 hours | Yes No |  |  | Yes No
Refrigeration circuit
Strength tested under F-gas legislation | Yes No |  |  | Yes No
Leak tested under F-gas legislation | Yes No |  |  | Yes No
Vacuum achieved | TBC |  |  | TBC
Maintained for 30 minutes | Yes No |  |  | Yes No
Refrigerant
Refrigerant type | TBC |  |  | TBC
Pipe Sizes (Main) | TBC |  |  | TBC
Pipe Sizes (Branch) | TBC | TBC | TBC | TBC | TBC | TBC
refrigerant circuit length - main pipes | TBC |  |  | TBC
Refrigerant circuit length - branch pipes | TBC | TBC | TBC | TBC | TBC | TBC
Additional refrigerant added | 0 |  |  | 0
Factory refrigerant charge (kg) | 0 |  |  | 0
Total system refrigerant charge (kg) | 0 |  |  | 0
Running tests (C/H) @ test condition | Cool / Heat | Cool / Heat | Cool / Heat | Cool / Heat | Cool / Heat | Cool / Heat
02 return air temperature | Required | Required | Required | Required | Required | Required
03 indoor coil - liquid temperature | Required | Required | Required | Required | Required | Required
04 indoor coil - vapour temperature | Required | Required | Required | Required | Required | Required
60 outdoor coil - liquid temperature | Required |  |  | Required
61 ambient temperature | Required |  |  | Required
62 compressor discharge temperature | Required |  |  | Required
63 compressor suction temperature | Required |  |  | Required
supply air temperature (HEAT & COOL) | Required | Required | Required | Required | Required | Required
Voltage across terminals L-N | Required |  |  | Required
Running current | Required |  |  | Required
Configurable items
03 network address | TBC |  |  | TBC
12 outdoor number | Required |  |  | Required
13 indoor unit number | Required | Required | Required | Required | Required | Required
14 indoor unit role | Required | Required | Required | Required | Required | Required
19 louver functions | Required | Required | Required | Required | Required | Required
5d air flow correction | Required | Required | Required | Required | Required | Required
Comments | Please read comments on pipe runs and pre-charge amounts for triple splits
Toshiba Air Conditioning, UTC House, Guildford Road, Leatherhead KT22 9UT Tel: 0870 8430333
Note on B4: Enter full site/store name
Note on B5: Enter full site address
Note on B21: Each day may be programmed separately, with up to 3 operating periods per day - if using scheduled timer
Note on B22: The network cable should be terminated in the indoor unit with Protocol Converter fitted. The screen shall be continuous and earthed at a single point. Minimum 1.5mm² up to 500m, 2.0mm² over 500m If a Protocol Converter has not been fitted, the cable should be left with enough slack for future use.
Note on B23: A single room sensor can be added to the group wiring and will provide the temperature value for the entire group. Configuration item 32 must remain at 0000
Note on B24: To enable group auto-restart, configuration item 28 to 0001.
Note on B25: Provides operating temperature value for the entire group. Configuration item 32 must be set to 0001. If the temperature sensor is enabled, the controller must be located in a representative position.
Note on B28: The style letter in the model number must be included i.e. 1104U = cassette, 1406B = ducted, 866K = hi-wall, 1107C = under-ceiling.
Note on B31: Identify Type of Outdoor Unit SM=Standard Digital Inverter SP=Super Digital Inverter
Note on B35: Suggested breaker sizes: SM140* - 25A SM160* - 32A SM2244 - 16A SM2804 - 20A SP140* - 25A SP140*AT8 - 16A SP160*AT8 - 16A
Note on B36: if applicable
Note on B37: Both liquid and vapour lines require full insulation (0 or 1 class).
Note on B38: Check that condensate is drained effectively. Circle PUMP if an external lift pump is used.
Note on B40: Only necessary for network control. A group will only have only one protocol converter fitted within the HEADER indoor unit.
Note on B41: Mains voltage should be supplied to the outdoor unit as soon as practical to warm the compressor.
Note on B43: Pressure should be increased in 3 stages - to ensure that the leak test may be conducted safely. Strength tested to not less than 1.3 x M.W.P
Note on B44: No maximum time for the leak test but there will be no drop in pressure during a successful test. Leak tested to 1.0 - 1.1 x M.W.P
Note on B45: The vacuum required will be dependant on the average temperature of the system (halfway between indoor and outdoor temperatures) A minimum of 4 Torr (530 Pa) should be achieved in all cases however, If the average temperature is below 10ºC a vacuum of 2 Torr (400 Pa) must be achieved. 5ºC requires a vacuum of a least 3 Torr (260 Pa) When below freezing point, the system cannot be reliably dehydrated
Note on B49: When systems are installed on 'existing' R22/R407c pipe work and the suction pipe is one step larger than standard, follow the 'Existing Pipe' instructions found within installation manual.
Note on B51: The linear (actual) length of the refrigeration pipe work between the outdoor unit and the 'Distributor' Note RAV-SM1603AT-E Max total pipe run is 50m (main + longest branch) Max length of a single branch must not exceed 15m, subtractive difference between branch lengths must not exceed 10m. RAV-SM2244-2804AT-E Max total pipe run is 70m (main + longest branch) irrespective of outdoor unit model Max length of a single branch must not exceed 20m, subtractive difference between branch lengths must not exceed 10m.
Note on B52: The total linear (actual) length of the refrigeration circuit - from Distributor to each indoor unit. Note RAV-SM1603AT-E Max total pipe run is 50m (main + longest branch) Max length of a single branch must not exceed 15m, subtractive difference between branch lengths must not exceed 10m. RAV-SM2244-2804AT-E Max total pipe run is 70m (main + longest branch) irrespective of outdoor unit model Max length of a single branch must not exceed 20m, subtractive difference between branch lengths must not exceed 10m.
Note on B53: The calculation's are DI For 1603AT outdoor units with 3 x 56* indoors (L1) Main Pipe minus 28m x 0.04kg/m = + (L2) Branch 1 minus 2m x 0.02kg/m = + (L3) Branch 2 minus 2m x 0.02kg/m = + (L4) Branch 3 minus 2m x 0.02kg/m = Additional charge =________ kg DI Big For 2244-2804AT outdoor units with 3 x 110*-140* indoors (L1) Main Pipe minus 28m x 0.08kg/m = + (L2) Branch 1 minus 2m x 0.04kg/m = + (L3) Branch 2 minus 2m x 0.04kg/m = + (L4) Branch 3 minus 2m x 0.04kg/m = Additional charge =________ kg Note DI/SDI range Min pipe run is 5m total Max run is 50m total irrespective of outdoor unit (L1 + L2 or L1 + L3 or L1 + L4) DI Big Range Min pipe run 7.5m total Max run is 70m total (L1 + L2 or L1 + L3 or L1 + L4) Always refer to the 'twin-kit' or installation manual
Note on B54: Factory refrigerant charge can be found on the name plate of the outdoor unit.
Note on B55: Total system charge is the additional charge plus the factory charge.
Note on B56: To initiate Press CHECK(Test) for 4 seconds. When the controller displays TEST, use mode to select heat or cool and use UNIT to choose the system to be tested. Note - systems MUST be tested individually. Values for both heating and cooling operations should be shown. This does not provide a 100% demand. To check values during test, (after compressor operation has started), press CHECK(Test)+CLEAR(CL). Press CHECK(Test) to terminate the test.
Note on B64: The temperature (DB) of the air supplied during the cooling and heating processes. Also known as air outlet temperature.
Note on B65: This measurement should be taken while the compressor is running.
Note on B66: Input current is limited by the inverter.
Note on B67: To access: Press CHECK(Test) & SET & CL buttons for 4 seconds
Note on B68: Only necessary when network control is used. Factory default 0099 May be set from the remote controller, through configuration item 03.
Note on B69: Automatically addressed though may be changed to reflect site reference.
Note on B70: Automatic addressing - generally 0001 unless twinned indoor units are used.
Note on B71: Individual system = 0000 Control group Header = 0001 (only 1 lead unit within a group) Follower = 0002 (up to a maximum of 7 followers)
Note on C51: L1 - From condenser to distributor
Note on C52: L2 - From distributor to indoor
Note on D52: L3 - From distributor to indoor
Note on E52: L4 - From distributor to indoor
Note on F51: L1 - From condenser to distributor
Note on F52: L2 - From distributor to indoor
Note on G52: L3 - From distributor to indoor
Note on H52: L4 - From distributor to indoor

## Quad Splits
TOSHIBA AIR CONDITIONING
Digital Inverter / Super Digital Inverter - ver c1.4
(Up to 2 x Quad systems)
Site/Store Name | TBC
Site Address | TBC
Commissioning Date | TBC
Installation company | TBC
Address | TBC
Telephone | TBC
e-mail | TBC
Commissioning Engineer | TBC
Training Certificate Number | TBC
Please forward to:
commissioning.uk@toshiba-ac.com
Local Controller Model | TBC
Local Controller Location | TBC
Sub controller model and location | TBC
Central Controller Model | TBC
Weekly Timer model | TBC
Time switch settings | TBC
Network cable (used with Central Controller) | TBC
Room sensor used? Location? | Yes / No
Configured for auto restart? | TBC
Configured for controller temp. sensor? | TBC
| 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Indoor model RAV-SM/SP****T-E | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
Indoor serial number | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
Indoor location or reference | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
Outdoor model RAV-SM/SP***AT-E | TBC |  |  |  | TBC
Outdoor serial number | TBC |  |  |  | TBC
Outdoor location or reference | TBC |  |  |  | TBC
Distribution board reference | TBC |  |  |  | TBC
Fuse size and type | TBC |  |  |  | TBC
Network address set from….. | TBC |  |  |  | TBC
Support and insulation effective | Yes No |  |  |  | Yes No
Condensate removal ok | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No
External pump fitted | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No
Protocol converter fitted | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No
Outdoor unit energised for 12 hours | Yes No |  |  |  | Yes No
Refrigeration circuit
Strength tested under F-gas legislation | Yes No |  |  |  | Yes No
Leak tested under F-gas legislation | Yes No |  |  |  | Yes No
Vacuum achieved | TBC |  |  |  | TBC
Maintained for 30 minutes | Yes No |  |  |  | Yes No
Refrigerant
Refrigerant type | TBC |  |  |  | TBC
Pipe Sizes (Main) | TBC |  |  |  | TBC
Pipe Sizes (Sub) | TBC |  | TBC |  | TBC |  | TBC
Pipe Sizes (Branch) | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
Refrigerant circuit length - Main pipe | TBC |  |  |  | TBC
Refrigerant circuit length - Sub pipes | TBC |  | TBC |  | TBC |  | TBC
Refrigerant circuit length - Branch pipes | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
Additional refrigerant added | 0 |  |  |  | 0
Factory refrigerant charge (kg) | 0 |  |  |  | 0
Total system refrigerant charge (kg) | 0 |  |  |  | 0
Running tests (C/H) @ test condition | Cool / Heat | Cool / Heat | Cool / Heat | Cool / Heat | Cool / Heat | Cool / Heat | Cool / Heat | Cool / Heat
02 return air temperature | Required | Required | Required | Required | Required | Required | Required | Required
03 indoor coil - liquid temperature | Required | Required | Required | Required | Required | Required | Required | Required
04 indoor coil - vapour temperature | Required | Required | Required | Required | Required | Required | Required | Required
60 outdoor coil - liquid temperature | Required |  |  |  | Required
61 ambient temperature | Required |  |  |  | Required
62 compressor discharge temperature | Required |  |  |  | Required
63 compressor suction temperature | Required |  |  |  | Required
supply air temperature (HEAT & COOL) | Required | Required | Required | Required | Required | Required | Required | Required
Voltage across terminals L1-L2/L1-L3/L2-L3 | Required |  |  |  | Required
Running current | Required |  |  |  | Required
Configurable items
03 network address | TBC |  |  |  | TBC
12 outdoor number | Required |  |  |  | Required
13 indoor unit number | Required | Required | Required | Required | Required | Required | Required | Required
14 indoor unit role | Required | Required | Required | Required | Required | Required | Required | Required
19 louver functions | Required | Required | Required | Required | Required | Required | Required | Required
5d air flow correction | Required | Required | Required | Required | Required | Required | Required | Required
Comments | Please read comments on pipe runs and additional charge amounts for quad splits
Toshiba Air Conditioning, UTC House, Guildford Road, Leatherhead KT22 9UT Tel: 0870 8430333
Note on B4: Enter full site/store name
Note on B5: Enter full site address
Note on B21: Each day may be programmed separately, with up to 3 operating periods per day - if using scheduled timer
Note on B22: The network cable should be terminated in the indoor unit with Protocol Converter fitted. The screen shall be continuous and earthed at a single point. Minimum 1.5mm² up to 500m, 2.0mm² over 500m If a Protocol Converter has not been fitted, the cable should be left with enough slack for future use.
Note on B23: A single room sensor can be added to the group wiring and will provide the temperature value for the entire group. Configuration item 32 must remain at 0000
Note on B24: To enable group auto-restart, configuration item 28 to 0001.
Note on B25: Provides operating temperature value for the entire group. Configuration item 32 must be set to 0001. If the temperature sensor is enabled, the controller must be located in a representative position.
Note on B28: The style letter in the model number must be included i.e. 1104U = cassette, 1406B = ducted, 866K = hi-wall, 1107C = under-ceiling.
Note on B31: Identify Type of Outdoor Unit SM=Standard Digital Inverter SP=Super Digital Inverter
Note on B35: Suggested breaker sizes: SM2244 - 16A SM2804 - 20A
Note on B36: if applicable
Note on B37: Both liquid and vapour lines require full insulation (0 or 1 class).
Note on B38: Check that condensate is drained effectively. Circle PUMP if an external lift pump is used.
Note on B40: Only necessary for network control. A group will only have only one protocol converter fitted within the HEADER indoor unit.
Note on B41: Mains voltage should be supplied to the outdoor unit as soon as practical to warm the compressor.
Note on B43: Pressure should be increased in 3 stages - to ensure that the leak test may be conducted safely. Strength tested to not less than 1.3 x M.W.P
Note on B44: No maximum time for the leak test but there will be no drop in pressure during a successful test. Leak tested to 1.0 - 1.1 x M.W.P
Note on B45: The vacuum required will be dependant on the average temperature of the system (halfway between indoor and outdoor temperatures) A minimum of 4 Torr (530 Pa) should be achieved in all cases however, If the average temperature is below 10ºC a vacuum of 2 Torr (400 Pa) must be achieved. 5ºC requires a vacuum of a least 3 Torr (260 Pa) When below freezing point, the system cannot be reliably dehydrated
Note on B49: When systems are installed on 'existing' R22/R407c pipe work and the suction pipe is one step larger than standard, follow the 'Existing Pipe' instructions found within installation manual.
Note on B52: The linear (actual) length of the refrigeration pipe work between the outdoor unit and the 1st 'T Piece' RAV-SM2244-2804AT-E Max total pipe run must not exceed 70m (main + longest sub + longest branch), irrespective of outdoor unit model.
Note on B53: The linear (actual) length of the refrigeration pipe work from sub pipe plus branch pipe Max total pipe run of (sub plus branch) -L2 + L4 or -L2 + L5 or -L3 + L6 or -L3 + L7 must not exceed 20m
Note on B54: The linear (actual) length of the refrigeration pipe work from the final 'T' Piece to the associated indoor unit. Max total pipe run of any branch pipe L4,L5,L6 or L7 must not exceed 15m Note (L4 + L2) minus (L5 + L2) or (L4 + L2) minus (L6 + L3) or (L4 + L2) minus (L7 + L3) or (L5 + L2) minus (L6 + L3) or (L5 + L2) minus (L7 + L3) or (L6 + L3) minus (L7 + L3) Must not exceed 6m
Note on B55: Calculation for RAV-SM2244AT8-E is; (Main Pipe) L1 minus 28m x 0.08 kg/m = + (Sub Pipe) L2 + L3 minus 4m x 0.04 kg/m = + (Branch Pipe) L4 + L5 + L6 + L7 x 0.02 kg/m = Additional charge =________kg Calculation for RAV-SM2804AT8-E is; (Main Pipe) L1 minus 28m x 0.08 kg/m = + (Sub Pipe) L2 + L3 minus 4m x 0.04 kg/m = + (Branch Pipe) L4 + L5 + L6 + L7 x 0.04 kg/m = Additional charge =________kg
Note on B56: Factory refrigerant charge can be found on the name plate of the outdoor unit.
Note on B57: Total system charge is the additional charge plus the factory charge.
Note on B58: To initiate Press CHECK(Test) for 4 seconds. When the controller displays TEST, use mode to select heat or cool and use UNIT to choose the system to be tested. Note - systems MUST be tested individually. Values for both heating and cooling operations should be shown. This does not provide a 100% demand. To check values during test, (after compressor operation has started), press CHECK(Test)+CLEAR(CL). Press CHECK(Test) to terminate the test.
Note on B66: The temperature (DB) of the air supplied during the cooling and heating processes. Also known as air outlet temperature.
Note on B67: This measurement should be taken while the compressor is running.
Note on B68: Input current is limited by the inverter.
Note on B69: To access: Press CHECK(Test) & SET & CL buttons for 4 seconds
Note on B70: Only necessary when network control is used. Factory default 0099 May be set from the remote controller, through configuration item 03.
Note on B71: Automatically addressed though may be changed to reflect site reference.
Note on B72: Automatic addressing - generally 0001 unless twinned indoor units are used.
Note on B73: Individual system = 0000 Control group Header = 0001 (only 1 lead unit within a group) Follower = 0002 (up to a maximum of 7 followers)
Note on C52: L1- From condenser to T piece
Note on C53: L2 - From 1st T piece to 2nd T piece (left)
Note on C54: L4 - From final T piece to fan coil
Note on D54: L5 - From final T piece to fan coil
Note on E53: L3- from 1st T piece to 2nd T piece (right)
Note on E54: L6 - From final T piece to fan coil
Note on F54: L7 - From final T piece to fan coil
Note on G52: L1- From condenser to T piece
Note on G53: L2 - From 1st T piece to 2nd T piece (left)
Note on G54: L4 - From final T piece to fan coil
Note on H54: L5 - From final T piece to fan coil
Note on I53: L3- from 1st T piece to 2nd T piece (right)
Note on I54: L6 - From final T piece to fan coil
Note on J54: L7 - From final T piece to fan coil

## VRF
TOSHIBA AIR CONDITIONING
VRF Start-Up Check Sheet - ver c1.4
SHRMi / SHRMe / SMMSi / SMMSe / Mini-SMMS
Please forward to : |  | commissioning.uk@toshiba-ac.com
Store Number |  |  |  | Date |  |  | Installer
Site Address
Distributor | [6 empty] | Branch
Installation Comprises of;
Outdoor Units |  | Model N° |  |  | Serial N° |  |  | Reference
|  | Model N° |  |  | Serial N° |  |  | Reference
|  | Model N° |  |  | Serial N° |  |  | Reference
|  | Model N° |  |  | Serial N° |  |  | Reference
Indoor Units |  | Qty (total)
N° FS Boxes RBM |  | -Y1123FE | Qty |  | -Y1803FE | Qty |  | -Y2803FE | Qty
|  | -Y1124FE | Qty |  | -Y1804FE | Qty |  | -Y2804FE | Qty
|  | -Y1801F4PE | Qty |  | -Y1801F6PE | Qty |  |  | Qty
Controls |  | RBC-AMT32E | Qty |  | RBC-AMS41E | Qty |  | RBC-AMS54E-ES | Qty
|  | RBC-AS41E2 | Qty |  | TCB-EXS21TLE | Qty |  | RBC-AX31U(W)-E | Qty
|  | TCB-AX21E2 | Qty |  | TCB-AX22CE2 | Qty |  | TCB-SC642TLE2 | Qty
BMS Options |  | TP0604ACE | Qty |  | TP5120ACE | Qty |  | TP0604TWE | Qty
|  | LSV2E | Qty |  | STCC01E | Qty |  | IFLSV1E | Qty
|  | IFWH3E | Qty |  | IFDD01E | Qty |  |  | Qty
Prior To Operating The System;
The crankcase heater has been energised for a minimum of 12 hours prior to start up. | [9 empty] | Yes \ No
All pipes are separately insulated and supported throughout the installation | [9 empty] | Yes \ No
The installation has been strength tested to (inc oil balance line) |  |  |  |  | Psig \ Bar |  | For a duration of |  |  | Hours
The installation has been leak tested to (inc oil balance line) |  |  |  |  | Psig \ Bar |  | For a duration of |  |  | Hours
The installation has been evacuated to (inc oil balance line) |  |  |  |  | Torr \ mBar |  | For a duration of |  |  | Hours
The installation has been maintained at (inc oil balance line) |  |  |  |  | Torr \ mBar |  | For a duration of |  |  | Hours
The equipment has been clearly labelled at the time of start-up | [9 empty] | Yes \ No
As installed drawing available | [9 empty] | Yes \ No
System Checks
Are all the service valves fully open? |  |  |  | Yes \ No | Heating & Cooling modes operate correctly? |  |  |  |  | Yes \ No
Access panels refitted? |  |  |  | Yes \ No | Condensate drainage correct? |  |  |  |  | Yes \ No
All compressors operating normally? |  |  |  | Yes \ No | Remote controller fault test? |  |  |  |  | Yes \ No
All outdoor fans operating normally? |  |  |  | Yes \ No | Group operation correct (where applicable)? |  |  |  |  | Yes \ No
Add charge recorded on label provided? |  |  |  | Yes \ No | Central operation correct (where applicable)? |  |  |  |  | Yes \ No
All indoor fans operating normally? |  |  |  | Yes \ No
SMMSi/e priority mode set at Heating * Cooling * Majority Operation * Specific Indoor unit *
The customer has been shown how to operate the equipment? | [9 empty] | Yes \ No
Operating Instruction have been left with the equipment? | [9 empty] | Yes \ No
INDOOR UNITS
| Installed Equipment Indoors |  |  |  | Cooling Mode |  |  | Heating Mode
| Model | Serial | Add | Reference | Return Air |  | Supply Air | Return Air |  | Supply Air
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
Indoor unit data continues on next page
Indoor units continued
| Installed Equipment Indoors |  |  |  | Cooling Mode |  |  | Heating Mode
| Model | Serial | Add | Reference | Return Air |  | Supply Air | Return Air |  | Supply Air
54
55
56
57
58
59
60
61
62
63
64
Indoor Pipe work Details
ADDITIONAL REFRIGERANT
Measure the total liquid line pipe lengths for each different diameter.
Total length 1/4" liquid pipe (meters) |  |  |  |  | Additional refrigerant added |  |  |  |  | KG
Total length 3/8" liquid pipe (meters)
Total length 1/2" liquid pipe (meters) |  |  |  |  | Note:
Total length 5/8" liquid pipe (meters) |  |  |  |  | Additional refrigerant charges must be calculated using formula found within installation manual supplied with condenser
Total length 3/4" liquid pipe (meters)
Total length 7/8" liquid pipe (meters) |  |  |  |  | A TRIM CHARGE & INDOOR UNIT CHARGE MAY FORM PART OF ADDITIONAL GAS CALCULATIONS.
ELECTRICAL and OPERATION
Electrical installation must be in accordance with all local and national regulations
Outdoor Unit |  | Breaker size |  | Type | Cable size mm² |  | Type
Header
Follower
Follower
Follower
Interconnecting (U1&U2, U5&U6) cable size | [5 empty] | mm | Type
Indoor unit power cable size | [5 empty] | mm | Type |  |  | Amp Fuse
Local controller cable size | [5 empty] | mm | Type
Electrical installation must be in accordance with all local and national regulations
Outdoor unit Performance Tests
Electrical Tests
Outdoor Unit |  | Header |  | Follower | Follower | Follower
L1 + N (volts)
L2 + N (volts)
L3 + N (volts)
L1 + L2 (volts)
L1 + L3 (volts)
L2 + L3 (volts)
L1 full load amps
L2 full load amps
L3 full load amps
Running Tests
Cooling Air On °C
Cooling Air Off °C
Heating Air On °C
Heating Air Off °C
Discharge pressure | [7 empty] | Psig \ Bar
Liquid pressure | [7 empty] | Psig \ Bar
Suction pressure | [7 empty] | Psig \ Bar
Comments
Commissioning Engineers Signature
Print Name
Training Certificate Number
Company
Note on C52: Full model reference to be entered
Note on D52: Complete serial number must be entered
Note on E13: Full model reference
Note on E14: Full model reference
Note on E15: Full model reference
Note on E16: Full model reference
Note on E52: Address noted from centre of local controller display while obtaining sensor data. Example: 1-1 or 2-13
Note on E125: X 0.025 kgs per/m
Note on E126: X 0.055 kgs per/m
Note on E127: X 0.105 kgs per/m
Note on E128: X 0.160 kgs per/m
Note on E129: X 0.250 kgs per/m
Note on E130: X 0.350 kgs per/m
Note on F31: Tested under current F-Gas regulations Pressure should be increased in 3 stages - to ensure that the leak test may be conducted safely. Strength tested to not less than 1.3 x M.W.P
Note on F32: Tested under current F-Gas regulations No maximum time for the leak test but there will be no drop in pressure during a successful test. Leak tested to 1.0 - 1.1 x M.W.P
Note on F33: The vacuum required will be dependant on the average temperature of the system (halfway between indoor and outdoor temperatures) A minimum of 4 Torr (530 Pa) should be achieved in all cases however, If the average temperature is below 10ºC a vacuum of 2 Torr (400Pa) must be achieved. 5ºC requires a vacuum of a least 3 Torr (260Pa) When below freezing point, the system cannot be reliably dehydrated.
Note on F52: Your reference used to identify unit/group. Example Room 103 Canteen unit
Note on G52: Obtained from CODE 02 within data retrieval menu at standard local controller. Or by use of air probe positioned at return air grille
Note on H13: Complete serial number must be entered.
Note on H14: Complete serial number must be entered.
Note on H15: Complete serial number must be entered.
Note on H16: Complete serial number must be entered.
Note on I52: Obtained by use of air probe positioned in air outlet vent. Controller set to TEST COOL beforehand.
Note on J20: Additional accessories to be entered
Note on J26: Additional accessories to be entered
Note on J52: Obtained from CODE 02 within data retrieval menu at standard local controller. Or by use of air probe positioned at return air grille
Note on J125: Total additional gas charge Mini SMMS, SMMS & SMMSi liquid pipe + trim = additional SMMSe liquid pipe + indoor unit ammount + trim = additional SHRM & SHRMi (liquid pipe x 1.3) + trim = additional
Note on L52: Obtained by use of air probe positioned in air outlet vent. Controller set to TEST HEAT beforehand.